## 错误码 (hidden)
返回首页
| Error Code | LCD Display | LCD显示 | Inverter State | 故障描述 | 中文描述 | 中文建议 | Fault Discription | English Suggestion
PV侧 | Error 200 | Error 200 | AFCI Fault | Error/Off | DC直流拉弧错误 | 直流拉弧异常 | 1:关机后检查面板端接线 2:重启逆变器 3:如果故障信息仍存在，联系制造商 | AFCI Fault | 1.After shutdown,Check the panel terminal. 2.Restart inverter. 3.If error message still exists,contact manufacturer.
| Error 201 | Error 201 | Residual I High | Error/Off | 漏电流GFCI过高 | 漏电流过高 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | Leakage current too high. | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 202 | Error 202 | PV Voltage High | Error/Off | 输入PV电压过高 | 面板电压过高 | 1:立刻断开DC开关并确认电压 2:恢复正常电压后，如果故障信息仍存在，联系制造商 | The DC input voltage is exceeding the maximum tolerable value. | 1.Immediately disconnect the DC switch and check the voltage 2:.If the fault code still exists after the normal voltage is restored, contact manufacturer
| Error 203 | Error 203 | PV Isolation Low | Error/Off | 面板绝缘阻抗ISO过低 | 面板绝缘阻抗低 | 1:关机后检查面板外壳是否可靠接地. 2:如果故障信息仍存在，联系制造商 | PV Isolation Low | 1.After shutdown,Check if panel enclosure ground properly. 2.If error message still exists,contact manufacturer.
AC侧 | Error 300 | Error 300 | AC V Outrange | Error/Off | 市电电压超过允许范围 | 市电电压异常 | 1:检查电网电压 2:如果电网电压已恢复至允许范围，故障信息仍存在，联系制造商 | AC V Outrange | 1.Check grid voltage. 2.If the error message still exists despite the grid voltage being within the tolerable range, contact manufacturer.
| Error 301 | Error 301 | AC reversed | Error/Off | 裂相电网/离网并机 | AC接线错误 | 1:请检查市电端 2:如果故障信息仍存在，联系制造商 | AC terminals reversed | 1:Check AC terminals 2:If error message still exists,contact manufacturer.
| Error 302 | Error 302 | No AC Connection | Error/Off | 输出端未连接市电 | 无市电连接 | 1:关机后检查交流侧线路连接 2:如果故障信息仍存在，联系制造商 | No AC Connection | 1.After shutdown,Check AC wiring. 2.If error message still exists,contact manufacturer.
| Error 303 | Error 303 | PE abnormal | Error/Off | 零地侦测异常 | 零地侦测异常 | 1. 关机后检查地线，确保地线连接可靠. 2:如果故障信息仍存在，联系制造商 | PE abnormal | 1.Check PE,to ensure that the PE line contact good. 2.If error message still exisits,contact Manufacturer
| Error 304 | Error 304 | AC F Outrange | Error/Off | 市电频率超范围 | 市电频率异常 | 1:检测电网频率，重启 2:如果故障信息仍存在，联系制造商 | AC F Outrange | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 305 | Error 305 | Over Load | Error/Off | 输出输出载率过大 | 输出过载保护 | 1：检查输出负载，减小负载功率 2：如果故障信息仍存在，联系制造商 | Over Load Fault | 1.Check whether output load over range; If load too large, please reduce load 2.If error message still exists, contact manufacturer.
| Error 306 | Error 306 | CT LN Reversed | Error/Off | 电流互感器反接 | 电流互感器反接 | 1：关机后检查电流互感器连接方向 2：如果故障信息仍存在，联系制造商 | CT LN Reversed | 1：After shutdown，Check the SP-CT connection. 2：If error message still exists,contact manufacturer.
| Error 307 | Error 307 | CT COM Fault | Error/Off | 通讯版和电流互感器通讯失败 | 电流互感器通讯失败 | 1：请检查通讯线 2：如果故障信息仍存在，联系制造商 | Communication fault，M3 didn't receive SP-CT data | 1：Check communication wire 2：If error message still exists,contact manufacturer.
| Error 308 | Error 308 |  | Error/Off | 机器与电流互感器配对超时 | 配对超时 | 1：机器与电流互感器配对超时，重新配对 2：如果故障信息仍存在，联系制造商 | Communication fault;Pairing time too long | 1：Restart pairing 2：If error message still exists,contact manufacturer.
| Error 311 | Error 311 | BackflowTimeOut | Error/Off | 基于N4105安规电表逆流功率控制超出范围超时保护 | 逆流功率溢出控制超时保护 | 1：关机后检查电流互感器连接方向 2：如果故障信息仍存在，联系制造商 | Backflow Power Overflow Control TimeOut | 1：After shutdown，Check the CT or meter connection. 2：If error message still exists,contact manufacturer.
系统内部 | Error 400 | Error 400 |  | Error/Off | 直流分量偏置电压异常 | 直流分量偏置异常 | 1.重启逆变器 2.如果故障信息仍存在，联系制造商 | DCI bias abnormal | 1.Restart inverter 2.If error message still exists, contact manufacturer.
| Error 401 | Error 401 |  | Error/Off | 输出电压直流分量过高 | 输出电压直流分量过高 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | DC Voltage High Fault | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 402 | Error 402 | Output High DCI | Error/Off | 输出电流直流分量过高 | 输出电流直流分量过高 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | Output DC current too high. | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 403 | Error 403 |  | Error/Off | 三相电流输出不平衡 | 输出电流不平衡 | 1:关机后检查输出电流是否不平衡 2:如果故障信息仍存在，联系制造商 | Output current unbalance | 1: After shutdown,Check the output current is not balanced. 2: If the error message still exists, contact manufacturer
| Error 404 | Error 404 |  | Error/Off | BUS电压采样异常 | 母线电压采样异常 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | bus sample fault | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 405 | Error 405 |  | Error/Off | 继电器异常 | 继电器异常 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | Relay fault | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 406 | Error 406 |  | Error/Off | 初始化模式错误 | 初始化模式异常 | 1:重新设置模式 2:如果故障信息仍存在，联系制造商 | Init model fault | 1.Reset mode 2.If error message still exists,contact manufacturer.
| Error 407 | Error 407 |  | Error/Off | 自动检测失败 | 自动检测失败 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | AutoTest failure | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 408 | Error 408 |  | Error/Off | 温度过高 | 温度过高 | 1.关机后检查温度，正常后重启逆变器 2.如果故障信息仍存在，联系制造商 | NTC Temperature too high | 1. .After shutdown,Check the temperature, normal restart the inverter 2. If the error message still exists, contact manufacturer
| Error 409 | Error 409 |  | Error/Off | BUS电压异常 | 母线电压异常 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | Bus voltage abnormal | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 410 | Error 410 |  | Error/Off | DSP和M3对绝缘阻抗采样不一致 | 绝缘阻抗采样不一致 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | Redundant sample circuit of Insulation values are different | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 411 | Error 411 |  | Error/Off | 内部通讯错误 | 内部通讯异常 | 1:关机后检查通讯版接线 2:如果故障信息仍存在，联系制造商 | Communication fault | 1.After shutdown,Check communication board wiring 2. If the error message still exists, contact manufacturer
| Error 412 | Error 412 | 控制板与通讯板 | Error/Off | NTC OPEN 温度传感器连接异常 | 温度传感器连接异常 | 1.关机后检查温度采样模块是否接好 2.如果故障信息仍存在，联系制造商 | Temperature sensor connection is abnormal | 1.After shutdown,Check the temperature sampling module is connected properly 2.If the error message still exists, contact manufacturer
| Error 413 | Error 413 |  | Error/Off | IGBT驱动异常 | 驱动异常 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | IGBT drive fault | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 414 | Error 414 |  | Error/Off | 存储器EEPROM读写错误 | 存储器异常 | 1.重启逆变器 2.如果故障信息仍存在，联系制造商 | EEPROM fault | 1.Restart inverter 2.If error message still exists, contact manufacturer.
| Error 415 | Error 415 |  | Error/Off | sps 异常 | 辅助电源异常 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | Internal power test fail（PV Power low） | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 416 | Error 416 |  | Error/Off | 直流/交流 过流保护 | 过流保护 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | Over current protected by software | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 417 | Error 417 |  | Error/Off | DSP和M3对电网电压采样不一致 | 电网电压采样不一致 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | Grid voltage sampling is inconsistent | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 418 | Error 418 |  | Error/Off | 控制板与通讯板固件版本不匹配 | 控制板与通讯板固件版本不匹配 | 1:检查固件版本 2:如果故障信息仍存在，联系制造商 | DSP and COM firmware version unmatch | 1.Check the firmware version. 2.If error message still exists,contact manufacturer.
| Error 419 | Error 419 |  | Error/Off | DSP和M3对漏电流采样不一致 | 漏电流采样不一致 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | Redundant sample circuit of GFCI values are different | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 420 | Error 420 |  | Error/Off | 漏电流检测模块有异常 | 漏电流模块异常 | 1:关机后检查漏电流模块 2:如果故障信息仍存在，联系制造商 | GFCI Module damage | 1: After shutdown,Check the leakage current module 2: If the error message still exists, contact manufacturer
| Error 421 | Error 421 |  | Error/Off | CPLD模块异常 | CPLD异常 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | CPLD is abnormal | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 422 | Error 422 |  | Error/Off | PV采样，正负bus采样，三相AC电压采样，GFCI，ISO采样中的某一个错误触发 | 冗余采样不一致 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | sampling is inconsistent | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 423 | Error 423 |  | Error/Off | 电池反接保护管异常 | 电池反接保护管异常 | 1.重启逆变器 2.如果故障信息仍存在，联系制造商 | Battery Reverse Protect Fault | 1.Restart inverter 2.If error message still exists, contact manufacturer.
| Error 424 | Error 424 |  | Error/Off | DSP和M3对电池电压采样不一致 | 电池电压采样不一致 | 1：重启机器 2：如果故障信息仍存在，联系制造商 | Communication board and control panel sampling battery voltage is inconsistent | 1.Restart inverter 2.If error message still exists, contact manufacturer.
| Error 425 | Error 425 |  | Error/Off | AFCI自检错误 | AFCI自检错误 | 1：重启机器 2：如果故障信息仍存在，联系制造商 | AFCI self-test fault | 1.Restart inverter 2.If error message still exists, contact manufacturer.
电池侧 | Error 500 | Error 500 | BMS COM Fault | Error/Off | 机器与电池通讯故障 | 电池通讯失败 | 1:重启整个系统 2:如果故障信息仍存在，联系制造商 | BMS Communication fault | 1.Check 485 cable between SP and battery 2.Check if battery is sleeping 3.If error message still exists,contact manufacturer.
| Error 501 | Error 501 | BMS Error | Error/Off | 电池报错不能充放电，根据电池错误码确定错误原因 | 电池报错 | 1：电池报错不能充放电，根据电池错误码确定错误原因 2：如果故障信息仍存在，联系制造商 | BMS failure and neither charge and discharge is allowe | 1：Depend on BMS error code 2：If error message still exists,contact manufacturer.
| Error 502 | Error 502 | Bat Voltage Low | Error/Off | 电池电压低 | 电池电压低 | 1：检查电池电压 2：如果故障信息仍存在，联系制造商 | Battery voltage low | 1：Check battery voltage 2：If error message still exists,contact manufacturer.
| Error 503 | Error 503 | Bat Voltage High | Error/Off | 电池电压过高 | 电池电压过高 | 1：检查电池电压是否正常，不正常请更换电池 2：如果故障信息仍存在，联系制造商 | Battery Voltage High | 1：Check whether the battery volttage too high; if battery OK, please restart the inverter; if not, please replace battery 2：If error message still exists,contact manufacturer.
| Error 504 | Error 504 | Bat Over Temp | Error/Off | 电池温度超范围 | 电池温度超范围 | 1：电池温度超出可充放电温度范围（可设置），检查电池温度 2：如果故障信息仍存在，联系制造商 | Battery temperature out of specified range for charge or discharge | 1.Check battery temperature 2.If error message still exists,contact manufacturer.
| Error 505 | Error 505 | Bat Reversed | Error/Off | 电池反接 | 电池反接 | 1:检查电池端 2:如果故障信息仍存在，联系制造商 | Battery terminals reversed | 1:Check battery terminals 2:If error message still exists,contact manufacturer.
| Error 506 | Error 506 | Battery Open | Error/Off | 电池未接或者接线未接好 | 电池开路 | 1:检查电池端 2:如果故障信息仍存在，联系制造商 | Battery terminal open (only for lithium battery) | 1:Check battery terminal 2:If error message still exists,contact manufacturer.
| Error 507 | Error 507 | Li-BAT Over Load | Error/Off | 负载功率大于锂电池额定放电功率 | 锂电池过载保护 | 1：检查是否负载大于电池放电额定功率 2：如果故障信息仍存在，联系制造商 | Lithium battery Over Load Fault | 1：Check whether output load over Lithium battery rate power; If load too large, please reduce load 2：If error message still exists, contact manufacturer.
| Error 508 | Error 508 | BUS2 Volt Abnomal | Error/Off | 异常低：BUS2 低于 Vbat*17/3(5.667)-50V 异常高：BUS2 高于 Vbat*17/3(5.667)+50V | BUS2电压异常 | 1：重启逆变器 2：如果故障信息仍存在，联系制造商 | BUS2 Volt Abnomal | 1.Restart inverter 2.If error message still exists, contact manufacturer.
离网侧 | Error 600 | Error 600 | EPS OP Short | Error/Off | 离网输出短路 | 离网短路 | 1.重启逆变器 2.如果故障信息仍存在，联系制造商 | EPS OP Short Fault | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Error 601 | Error 601 | Buck Over Currrent | Error/Off | 光伏充电过流 | 光伏充电过流 | 1.重启逆变器 2.如果故障信息仍存在，联系制造商 | Buck Over Current Fault | 1.Restart inverter 2.If error message still exists, contact manufacturer.
| Error 602 | Error 602 | DC-DC Fault | Error/Off | 直流到直流转换异常 | 直流到直流转换异常 | 1.重启逆变器 2.如果故障信息仍存在，联系制造商 | DC-DC Fault | 1.Restart inverter 2.If error message still exists, contact manufacturer.
| Error 603 | Error 603 | Soft Start Fail | Error/Off | 软启动失败 | 软启失败 | 1：重启逆变器 2：如果故障信息仍存在，联系制造商 | Soft start run out of time | 1.Restart inverter 2.If error message still exists, contact manufacturer.
| Error 604 | Error 604 | Output Volt Low | Error/Off | 离网输出电压过低 | 离网输出电压过低 | 1：重启逆变器 2：如果故障信息仍存在，联系制造商 | Off-grid output voltage is too low | 1.Restart inverter 2.If error message still exists, contact manufacturer.
| Error 605 | Error 605 | Output Volt High | Error/Off | 离网输出电压过高 | 离网输出电压过高 | 1：重启逆变器 2：如果故障信息仍存在，联系制造商 | Off-grid output voltage is too High | 1.Restart inverter 2.If error message still exists, contact manufacturer.
Note on B2: 作者: 此处列出在历史记录中的故障代码，应和记录中的代码完全一致
Note on C2: 作者: 此处列出当机器出现故障时，LCD上显示的完整的故障信息。需和LCD上的显示信息完全一致。
Note on E2: 作者: 此处应说明机器在出现前面代码时，处于什么状态。警告并继续运行或者报错停机。若警告且继续运行可写：Warning/On；若错误且停机可写：Error/Off
Note on I2: 作者: 对前面的错误给出定义，并指出是哪部分出现故障

## 告警码 (hidden)
返回首页
| Warning Code | LCD Display | LCD显示 | Inverter State | 警告描述 | 中文描述 | 中文建议 | Fault Discription | English Suggestion
PV侧 | Warning 200 | Warning200 | String Fault | Warning/On | 多路组串不匹配， | 面板接入故障 | 1.关机后检查面板是否正常; 2.如果故障信息仍存在，联系制造商 | String fault | 1.After shutdown,Check the panel is normal. 2.If error message still exists, contact manufacturer.
| Warning 201 | Warning201 | Warning200 | Warning/On | 组串端子接线异常 | 组串/PID快接端子异常 | 1:关机后检查组串端子接线 2:如果故障信息仍存在，联系制造商 | String PID quick connect terminal detection error | 1.After shutdown,Check the string terminal wiring. 2. If the error message still exists, contact the manufacturer.
| Warning 202 | Warning202 | DC SPD warning | Warning/On | 直流防雷器 | 直流防雷器告警 | 1:关机后检查直流防雷器 2:如果故障信息仍存在，联系制造商 | DC SPD function abnormal | 1.After shutdown,Check the DC SPD. 2.If error message still exists,contact manufacturer.
| Warning 203 | Warning203 | PV Circuit short | Warning/On | 第一路或第二路面板或者线路是否短路 | 面板短路 | 1:检查第一路或第二路面板或者线路是否短路 2:如果故障信息仍存在，联系制造商 | PV Circuit short | 1：Check the PV1 or PV2 wiring is short-circuited 2：If error message still exists,contact manufacturer.
| Warning 204 | Warning204 | Warning202 | Warning/On | 干结点功能异常 | 干结点功能异常 | 1:关机后检查干结点接线 2:如果故障信息仍存在，联系制造商 | Dryconnect function abnormal | 1.After shutdown,Check the dry Dryconnect wiring. 2.If the error message still exists, contact manufacturer.
| Warning 205 | Warning205 | Warning204 | Warning/On | Boost升压驱动异常 | 升压驱动异常 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | PV Boost driver broken | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Warning 206 | Warning206 | AC SPD warning | Warning/On | 交流防雷器 | 交流防雷器告警 | 1:关机后检查直流防雷器 2:如果故障信息仍存在，联系制造商 | AC SPD function abnormal | 1.After shutdown,Check the AC SPD. 2.If error message still exists,contact manufacturer.
| Warning 207 | Warning207 | USB Over-Current | Warning/On | USB过流保护 | USB过流保护 | 1:拔掉U盘 2:关机后重新接入U盘 3:如果故障信息仍存在，联系制造商 | U disk over-current protection | 1: unplug the U disk 2: Re-access U disk after shutdown 3.If the error message still exists, contact manufacturer.
| Warning 208 | Warning208 | DC Fuse Open | Warning/On | 直流保险丝断开 | 直流保险丝断开 | 1:关机后检查保险丝 2:如果故障信息仍存在，联系制造商 | DC Fuse Open | 1.After shutdown,Check fuse. 2.If error message still exists, contact manufacturer.
| Warning 209 | Warning209 | PV Voltage High | Warning/On | 面板PV电压过高 | 面板电压过高 | 1:立刻断开DC开关并确认电压 2:恢复正常电压后，如果故障信息仍存在，联系制造商 | The DC input voltage is exceeding the maximum tolerable value. | 1.Immediately disconnect the DC switch and check the voltage 2:.If the fault code still exists after the normal voltage is restored, contact manufacturer
| Warning 210 | Warning210 | PV Reversed | Warning/On | 面板PV反接 | 面板反接 | 1:检查面板输入端 2:如果故障信息仍存在，联系制造商 | PV Reversed | 1:Check PV input terminals 2:If error message still exists,contact manufacturer.
AC侧 | Warning 300 | Warning300 | No AC Connection | Warning/On | 市电未接或接线未接好 | 无市电连接 | 1.请确认电网是否丢失。 2.如果故障信息仍存在，联系制造商 | No Utility | 1. Please confirm grid is lost or not. 2.If error message still exists,contact manufacturer.
| Warning 301 | Warning301 | AC V Outrange | Warning/On | 市电电压超范围 | 市电电压超范围 | 1.检查交流电压是否在标准电压的规格范围内。 2.如果故障信息仍存在，联系制造商 | Grid voltage outrange | 1.Check the AC voltage is in the range of standard voltage in specification. 2. If error message still exists,contact manufacturer.
| Warning 302 | Warning302 | AC F Outrange | Warning/On | 市电频率超范围 | 市电频率超范围 | 1.检查频率是否在范围内。 2.如果故障信息仍存在，联系制造商 | Grid frequency outrange | 1.Check the frequency is in the range of specification or not. 2.If error message still exists,contact manufacturer.
| Warning 303 | Warning303 | Over Load | Warning/On | 输出功率超范围 | 输出过载 | 1:减小输出功率 2:如果故障信息仍存在，联系制造商 | EPS mode, over load | 1.Please reduce the load of EPS output. 2.If error message still exists,contact manufacturer.
| Warning 304 | Warning304 | CT Open | Warning/On | 电流互感器没接或接线没接好 | 电流互感器开路 | 1:检查电流互感器是否连接好 2:如果故障信息仍存在，联系制造商 | CT Open | 1：Check if AC current sensor is connected well 2：If error message still exists,contact manufacturer.
| Warning 305 | Warning305 | SP-CT L N reversed | Warning/On | 电流互感器反接 | 电流互感器反接 | 1:检查电流互感器是否接反 2:如果故障信息仍存在，联系制造商 | SP-CT L N line reversed or Ground fail | 1：Check the L line and N line of SP-CT is reversed or not. 2：If error message still exists,contact manufacturer.
| Warning 306 | Warning306 | CT COM Fault | Warning/On | 机器与电流互感器通讯失败 | 电流互感器通讯失败 | 1：请检查通讯线 2：如果故障信息仍存在，联系制造商 | Communication fault，M3 didn't receive SP-CT data | 1：Check communication wire 2：If error message still exists,contact manufacturer.
| Warning 307 | Warning 307 | PairingTimeOut | Warning/On | 无线CT配对超时 | 无线CT配对超时 | 1：请检查通讯线 2：如果故障信息仍存在，联系制造商 | Communication fault | 1：Check communication wire 2：If error message still exists,contact manufacturer.
系统内部 | Warning 400 | Warning400 | Fan warning XXXX | Warning/On | XXXX分别对应四个风扇，正常工作为0000.某一个风扇错误就为1，例如0010表示第三个风扇错误 | 风扇功能异常 | 1:关机后检查风扇接线 2:更换风扇 3:如果故障信息仍存在，联系制造商 | Fan function abnormal | 1.After shutdown,Check the fan connection. 2. replace the fan. 3. If the error message still exists, contact manufacturer.
| Warning 401 | Warning401 | Warning403 | Warning/On | 电表和机器的通讯连接不正常 | 电表异常 | 1:检查电表是否打开 2：检查机器与电表的连接是否正常 | Meter abnormal | 1: Check if the meter is on 2: Check the machine and the meter connection is normal
| Warning 402 | Warning402 | Warning402 | Warning/On | 优化器和逆变器通讯异常 | 优化器和逆变器通讯异常 | 1.检查优化器是否打开。 2.检查优化器与逆变器的连接是否正常 | Optimizer and inverter communication is abnormal | 1. Check if the optimizer is on. 2. Check whether the connection between the optimizer and the inverter is normal.
| Warning 403 | Warning403 | Warning401 | Warning/On | 组串板通讯异常 | 组串通讯异常 | 1:关机后检查组串板接线 2:如果故障信息仍存在，联系制造商 | String communication abnormal | 1.After shutdown,Check the string panel wiring. 2. If the error message still exists, contact manufacturer .
| Warning 404 | Warning404 | Warning404 | Warning/On | 存储器EEPROM读写异常 | 存储器异常 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | EEPROM abnormal. | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Warning 405 | Warning405 | Warning405 | Warning/On | 控制板与通讯板固件版本不匹配 | 控制板与通讯板固件版本不匹配 | 1:检查固件版本 2:如果故障信息仍存在，联系制造商 | DSP and COM firmware version unmatch | 1.Check the firmware version. 2.If error message still exists,contact manufacturer.
| Warning 406 | Warning406 | Warning406 | Warning/On | boost升压电路故障 | 升压电路故障 | 1.重启逆变器 2.如果故障信息仍存在，联系制造商 | Boost module error | 1.Restart inverter 2.If error message still exists, contact manufacturer.
电池侧 | Warning 500 | Warning500 | BMS COM Warning | Warning/On | 机器与电池通讯故障 | 电池通讯故障 | 1.检查锂电池是否打开。 2.检查锂电池与逆变器的连接是否正常。 | SPH failed to communication with lithium battery | 1.Check the lithium Battery is open or not. 2.Check the connection of lithium Battery and inverter is good or not.
| Warning 501 | Warning501 | Battery Open | Warning/On | 电池接线未接好 | 电池未接 | 1:检查电池是否连接 2:如果故障信息仍存在，联系制造商 | Battery terminal open (only for lithium battery) | 1：Check the battery is connected 2：If error message still exists,contact manufacturer.
| Warning 502 | Warning502 | Warning：Bat High | Warning/On | 电池电压过高 | 电池电压过高 | 1：检查电池电压是否在规格范围内 2：检查电池是否连接好 3:如果故障信息仍存在，联系制造商 | Battery Voltage high | 1.Check the voltage of battery is in the range of specification or not. 2.Check the battery connection is right or not. 3.If error message still exists,contact manufacturer.
| Warning 503 | Warning503 | Warning：Bat Low | Warning/On | 电池电压过低 | 电池电压过低 | 1：检查电池电压是否在规格范围内 2：检查电池是否连接好 3:如果故障信息仍存在，联系制造商 | Battery Voltage Low | 1.Check the voltage of battery is in the range of specification or not. 2.Check the battery connection is right or not. 3.If error message still exists,contact manufacturer.
| Warning 504 | Warning504 | Battery reversed | Warning/On | 电池反接 | 电池反接 | 1:检查电池是否接反 2:如果故障信息仍存在，联系制造商 | Battery terminals reversed | 1：Check the positive and negative of battery is reversed or not. 2：If error message still exists,contact manufacturer.
| Warning 505 | Warning505 | BAT NTC Open | Warning/On | 电池温度检测未连接好 | 电池温度检测未接 | 1：检查电池温度检测是否安装 2：检测电池温度检测是否连接好 3:如果故障信息仍存在，联系制造商 | Lead-acid battery temperature sensor was open | 1.Check the temperature of lead-acid battery is installed or not.. 2.Check the temperature of lead-acid battery is connected well or not. 3：If error message still exists,contact manufacturer.
| Warning 506 | Warning506 | Bat temp outrange | Warning/On | 电池温度超过允许范围 | 电池温度超范围 | 1:检查电池环境温度是否在规格范围内 2:如果故障信息仍存在，联系制造商 | Battery temperature outrange | 1：Check the environment temperature of battery is in the range of specification or not. 2：If error message still exists,contact manufacturer.
| Warning 507 | Warning507 | BMS Error | Warning/On | 电池报错不能充放电，根据电池错误码确定错误原因 | 电池报错 | 1：电池报错不能充放电，根据电池错误码确定错误原因 2：如果故障信息仍存在，联系制造商 | BMS failure and neither charge and discharge is allowe | 1：Depend on BMS error code 2：If error message still exists,contact manufacturer.
| Warning 508 | Warning508 | Li-BAT Over Load | Warning/On | 负载功率大于锂电池额定放电功率 | 锂电池过载保护 | 1：检查是否负载大于电池放电额定功率 2：如果故障信息仍存在，联系制造商 | Lithium battery Over Load Fault | 1：Check whether output load over Lithium battery rate power; If load too large, please reduce load 2：If error message still exists, contact manufacturer.
| Warning 509 | Warning509 | BMS Warning :XXX | Warning/On | 电池管理系统信息异常 | 电池管理系统信息异常 | 1.重启逆变器 2.如果故障信息仍存在，联系制造商 | BMS Battery Msg Failure | 1.Restart inverter 2.If error message still exists, contact manufacture.
离网侧 | Warning 600 | Warning 600 | Output High DCI | Warning/On | 输出电流直流分量过高 | 输出直流分量偏置异常 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | DCI bias abnormal | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Warning 601 | Warning 601 | Output High DCV | Warning/On | 输出电压直流分量过高 | 输出电压直流分量过高 | 1:重启逆变器 2:如果故障信息仍存在，联系制造商 | DC Voltage High Fault | 1.Restart inverter. 2.If error message still exists,contact manufacturer.
| Warning 602 | Warning 602 | EPS Volt Low | Warning/On | 离网输出电压过低 | 离网输出电压过低 | 1：重启逆变器 2：如果故障信息仍存在，联系制造商 | Off-grid output voltage is too low | 1.Restart inverter 2.If error message still exists, contact manufacturer.

## 变更记录
版本 | 变更内容 | 更新人
V1.1 | 1.将 Residual I High由Warning变为Error，错误位由Byte1.3改为Byte12.6 2. 将 Relay fault 由Warning变为Error，错误位由Byte2.0改为Byte10.2 3.将 Warning 104 改为Error 104，错误位由Byte13.2改为Byte10.5. 4.Battery need Charge 和 Battery Full 改为不显示 5.将Byte5.0改为显示EPS Volt Low
V1.2 | 1.将Byte11.6和Byte11.7改为Byte0不报错只重启。 2.byte10.3和byte10.4改为不显示 3.添加 Fault or warning bit 方便通过监控检查报错。
V1.3 | 1.添加错误位中文解释 2.更新Byte0错误位，添加Master set restart PWM
V1.4 | 1.控制板与通讯板固件版本不匹配 从Error 417改为Error 418 2.系统错误位增加“电网电压采样不一致”Byte11.6 显示为Error 417 3.EPS侧增加Byte5.5错误DCV_High. 4.更新所有错误代码为公司统一代码。
V1.5 | 1.调整Errorlist byte10/11/12 的系统错误位,对应修改LCD显示错误码； 2.规范和统一变量命名； 3.更新错误码和告警码；
V1.6 | 电表错误从电池故障位byte7，移放到系统告警byte14
V1.7 | 新增Error 311为 逆流功率溢出超时保护 | 王飞

## MIX-Plus&US&SPH4-10K ErrorCode
Word definition |  |  | 逆变器故障码 | 逆变器告警码 | Total bit defined | LCD_Display | Server Monitor（old） | Monitor Chinese（old） | Fault or warning Data | M3 | INV | SP | comment | Action
System fault word0 | Byte0 | bit0 | Error 503 |  | BatVoltHigh_ISR |  |  |  | 1 |  |  |  | Internal fault | restart PWM
|  | bit1 |  |  | \ |  |  |  | 2 |  |  | Y
|  | bit2 | Error 508 |  | Bus2VoltHigh_ISR |  |  |  | 4 |  |  | Y
|  | bit3 | Error 409 |  | BusVoltHigh_ISR |  | BusVoltHigh_ISR | BUS电压过大 | 8 |  | Y
|  | bit4 | Error 416 |  | INVCurrOCP_TZ |  | INVCurrOCP_Mask | 逆变电流过大 | 16 |  | Y
|  | bit5 | 未使用 |  | FreqUnstable_Mask |  |  |  | 32 |  | Y
|  | bit6 | Error 416 |  | BBOCP_FaultISR |  | BBOCP_FaultISR_SP | buck_boost电流过大 | 64 |  |  | Y
|  | bit7 | Error 416 |  | BDCOCP_FaultTZ |  | BBOCP_FaultTZ_SP | buck_boost电流过大 | 128 |  |  | Y
| Byte1 | bit8 |  |  | GridZC_lossFault |  |  |  | 256 |  | Y |  | Grid side abnormal | Turn to Standby
|  | bit9 |  |  | \ |  |  |  | 512
|  | bit10 |  |  | \ |  |  |  | 1024
|  | bit11 |  |  | \ |  |  |  | 2048
|  | bit12 | Error 300 |  | GridR_VFault(Singlephase) | AC V Outrange | AC V Outrange | 市电电压超范围 | 4096 |  | Y
|  | bit13 | Error 300 |  | GridS_VFault | AC V Outrange | AC V Outrange | 市电电压超范围 | 8192
|  | bit14 | Error 300 |  | GridT_VFault | AC V Outrange | AC V Outrange | 市电电压超范围 | 16384
|  | bit15 | Error 304 |  | GridFFault | AC F Outrange | AC F Outrange | 市电频率超范围 | 32768 |  | Y
System fault word1 | Byte2 | bit0 |  |  | reserved |  |  |  | 1 |  |  |  | Grid side abnormal | Turn to Standby
|  | bit1 | Error 201 |  | GFCIDamage |  |  |  | 2
|  | bit2 | Error 300 |  | GridR_VLowFault | AC V Outrange | AC V Outrange | 市电电压超范围 | 4
|  | bit3 | Error 300 |  | GridR_VHighFault | AC V Outrange | AC V Outrange | 市电电压超范围 | 8
|  | bit4 | Error 300 |  | GridS_VLowFault | AC V Outrange | AC V Outrange | 市电电压超范围 | 16
|  | bit5 | Error 300 |  | GridS_VHighFault | AC V Outrange | AC V Outrange | 市电电压超范围 | 32
|  | bit6 | Error 300 |  | GridT_VLowFault | AC V Outrange | AC V Outrange | 市电电压超范围 | 64
|  | bit7 | Error 300 |  | GridT_VHighFault | AC V Outrange | AC V Outrange | 市电电压超范围 | 128
| Byte3 | bit8 | Error 416 |  | INVCurrOCP_ISR |  |  |  | 256 |  |  |  | Grid side abnormal | Turn to Standby
|  | bit9 |  |  | \ |  |  |  | 512
|  | bit10 |  |  | \ |  | Output High DCI | 直流分量偏置异常 | 1024 |  | Y
|  | bit11 |  |  | \ |  |  |  | 2048
|  | bit12 | Error 416 |  | INVR_CurrOCP_Rms |  |  |  | 4096
|  | bit13 | Error 416 |  | INVS_CurrOCP_Rms |  |  |  | 8192
|  | bit14 | Error 416 |  | INVT_CurrOCP_Rms |  |  |  | 16384
|  | bit15 | Error 302 |  | NoUtility | No AC Connection | No AC Connection | 无市电连接 | 32768 |  | Y
System fault word2 | Byte4 | bit0 | Error 304 |  | GridFLowFault | AC F Outrange | AC F Outrange | 市电频率超范围 | 1 |  |  |  | Grid side abnormal | Turn to Standby
|  | bit1 | Error 304 |  | GridFHighFault | AC F Outrange | AC F Outrange | 市电频率超范围 | 2
|  | bit2 | Error 313 |  | GridVolt_Unbalance_Fault |  |  |  | 4
|  | bit3 | 暂无 |  | AC_PLL_Fault |  |  |  | 8
|  | bit4 | 暂无 |  | OverLoadFault |  | OverLoadFault | 离网输出功率过大 | 16
|  | bit5 | Error 311 |  | BackflowTimeOut | BackflowTimeOut |  |  | 32
|  | bit6 |  |  | \ |  |  |  | 64
|  | bit7 |  |  | \ |  |  |  | 128
| Byte5 | bit8 | Error 604 |  | EPS_LineVoltR_Loss | U(E)PS Volt Low ！ | EPS Volt Low | 离网输出电压过低 | 256 |  | Y |  | EPS side abnormal | Turn to Standby
|  | bit9 | Error 604 |  | EPS_LineVoltS_Loss EPSOverWatt(单相机) | U(E)PS Volt Low ！ | EPS Volt Low | 离网输出电压过低 | 512
|  | bit10 | Error 604 |  | EPS_LineVoltT_Loss | U(E)PS Volt Low ！ | EPS Volt Low | 离网输出电压过低 | 1024
|  | bit11 | Error 409 |  | EPS_BusVoltLow |  | EPS_BusVoltLow | 离网BUS电压过低 | 2048 |  | Y
|  | bit12 | Error 607 |  | EPS_LoadAbnormal |  |  |  | 4096 |  | Y
|  | bit13 | Error 605 |  | EPS_LineVolt_High |  |  |  | 8192 |  | Y
|  | bit14 | Error 606 |  | DCV_High |  |  |  | 16384
|  | bit15 | 暂无 |  | Bat_OCP |  |  |  | 32768
System fault word3 | Byte6 | bit0 | Error 505 |  | BatTerminalReverse | Battery reversed | Battery reversed | 电池反接 | 1 |  |  | Y | BAT Side abnormal | Turn to Standby
|  | bit1 | Error 506 |  | BatTerminalOpen | Battery Open | Battery Open | 电池未接 | 2 |  |  | Y
|  | bit2 | Error 502 |  | BatVoltLow | Bat Voltage Low | Battery Voltage Low | 电池电压过低 | 4 |  |  | Y
|  | bit3 |  |  | \ |  | NV_OverTemp_Fault | 温度异常 | 8 |  |  | Y
|  | bit4 | Error 508 |  | BUS2Abnomal |  |  |  | 16
|  | bit5 | Error 429 |  | SoftStartFail |  | NV_OverTemp_Fault | 软起失败 | 32 |  |  | Y
|  | bit6 | Error 503 |  | BatVoltHigh | Bat Voltage High | Bat Voltage High | 电池电压过高 | 64 |  |  | Y
|  | bit7 | 暂无 |  | BatOverLoadFault | Bat overLoad |  |  | 128
| Byte7 | bit8 | Error 501 |  | BMSError | BMS Error:XXX | BMS Battery Msg Failure | 电池管理系统信息异常 | 256 | Y |  |  | BAT Side abnormal | Turn to Standby
|  | bit9 | Error 500 |  | BMS CommFault | BMS COM Fault | BMS Error:XXX | 电池通讯故障 | 512 | Y
|  | bit10 |  |  | \ |  | CT LN Reversed | 电流互感器反接 | 1024
|  | bit11 |  |  | \ |  | PairingTimeOut | 无线CT配对超时 | 2048
|  | bit12 |  |  | \ |  | Warn 401 | 通讯异常 | 4096
|  | bit13 | 暂无 |  | BatSleep |  | BatterySleep | 电池休眠 | 8192 | Y
|  | bit14 | 暂无 |  | BatNTCOpen | BAT NTC Open ! | LeadacidBatNTCOpen | 铅酸电池NTC未接 | 16384 | Y
|  | bit15 |  |  | BMSStateAbnormal |  |  |  | 32768
System fault word4 | Byte8 | bit0 |  |  | \ |  |  |  | 1 |  |  |  | PV Side Abnormal | Turn to Standby
|  | bit1 |  |  | \ |  |  |  | 2
|  | bit2 |  |  | \ |  |  |  | 4
|  | bit3 |  |  | \ |  |  |  | 8
|  | bit4 |  |  | \ |  |  |  | 16
|  | bit5 | 暂无 |  | PV1_VoltLowWarn |  | PV1VoltLowWarn | PV1低压警告 | 32 |  | Y
|  | bit6 | 暂无 |  | PV2-VoltLowWarn |  | PV2VoltLowWarn | PV2低压警告 | 64 |  | Y
|  | bit7 |  |  | \ |  |  |  | 128
| Byte9 | bit8 |  |  | \ |  |  |  | 256 |  |  |  | PV Side Abnormal | Turn to Standby
|  | bit9 |  |  | \ |  |  |  | 512
|  | bit10 |  |  | \ |  |  |  | 1024
|  | bit11 |  |  | \ |  |  |  | 2048
|  | bit12 |  |  | \ |  |  |  | 4096
|  | bit13 |  |  | \ |  |  |  | 8192
|  | bit14 |  |  | \ |  |  |  | 16384
|  | bit15 |  |  | \ |  |  |  | 32768
System fault word5 | Byte10 | bit0 | Error 402 |  | DCIHigh | Output High DCI | Error 303 | 零地侦测异常 | 1 |  |  | Y | Sytem fault | Turn to Standby
|  | bit1 | Error 203 |  | PVISOFault | PV Isolation Low | PV Isolation Low | 面板绝缘阻抗低 | 2 |  | Y
|  | bit2 | Error 412 |  | NTCOpenFault | NTC Open | Error 405 | 继电器异常 | 4 |  | Y
|  | bit3 | Error 409 |  | BusVoltHigh_Fault | Error：103！ | Error 417 | DSP和M3对电网电压采样不一致 | 8
|  | bit4 | Error 202 |  | PVVoltHigh_Fault | PV Voltage High! | Error 419 | BUS电压采样不一致 | 16
|  | bit5 | Error 408 |  | BTHeatsink_Overtemp | Error:408! | Error 418 | 控制板与通讯板固件版本不匹配 | 32 | Y
|  | bit6 | Error 408 |  | BBHeatsink_TempOver | Error:408! | Error 411 | 内部通讯异常 | 64 | Y
|  | bit7 | Error 408 |  | INVHeatsink_Overtemp | Error:408! | Error 411 | 内部通讯异常 | 128 | Y
| Byte11 | bit8 | Error 600 |  | EPS_OPShortFault | OP Short Fault ! | EPS OP Short Fault | 离网短路 | 256 |  | Y |  | Sytem fault | Turn to Standby
|  | bit9 | Error 407 |  | AuotTestFault | Error 407 | Error 407 | 自动检测失败 | 512 |  | Y
|  | bit10 | Error 406 |  | ModelFault | Error 406 | Init model fault | 初始化模式异常 | 1024 |  | Y | Y
|  | bit11 | Error 405 |  | RelayFault | Error 405 | NTC Open | 温度异常 | 2048 |  | Y | Y
|  | bit12 | Error 428 |  | BusUnbalance_Fault | BusUnbalance |  |  | 4096 |  |  | Y
|  | bit13 | Error 418 |  | DSP_M3FWUnmatch | Error 418 |  |  | 8192 |  |  | Y
|  | bit14 |  | Warning 203 | PV1Short_Fault | Warning 203 |  |  | 16384
|  | bit15 |  | Warning 203 | PV2Short_Fault | Warning 203 |  |  | 32768
System fault word6 | Byte12 | bit0 | Error 303 |  | NEDetectFault | Error 303 | PVVoltHigh_Fault | PV1电压过高 | 1 |  | Y |  | Sytem fault | Turn to Standby
|  | bit1 |  |  | AFCICheckFault（US） |  | PV2_VoltHighFault | PV2电压过高 | 2
|  | bit2 | Error 411 |  | AComFault | Error 411 | Over Temperature | 温度异常 | 4 |  | Y
|  | bit3 | Error 411 |  | BComFault AFCIFault（US） | Error 411 | Over Temperature | 温度异常 | 8 |  | Y
|  | bit4 | 暂无 |  | MasterForceINVFault |  | MasterForceINVFault | INV发生故障 | 16 |  | Y
|  | bit5 | 暂无 |  | MasterForceSPFault |  | MasterForceSPFault | SP发生故障 | 32 |  |  | Y
|  | bit6 | Error 201 |  | GFCIHigh | Residual I High | Leakage current too high | 漏电流过高 | 64 |  | Y
|  | bit7 | 暂无 |  | VirLoad_Overtemp | VirLoad TempOver |  |  | 128
| Byte13 | bit8 |  | Warning 205 | BoostDriver1Warn | 不显示 |  |  | 256 |  |  |  | System warning | Turn to Standby
|  | bit9 |  | Warning 205 | BoostDriver2Warn | 不显示 |  |  | 512
|  | bit10 |  |  | \ |  |  |  | 1024
|  | bit11 |  |  | SPDFault | SPD Fault | Warning 203 | PV端短路告警 | 2048 |  | Y
|  | bit12 |  |  | \ |  | Warning 203 | PV端短路告警 | 4096 |  | Y
|  | bit13 |  |  | \ |  | Warn 101 | 无线CT/电表通信异常 | 8192
|  | bit14 |  |  | \ |  |  |  | 16384
|  | bit15 |  |  | EPSoverLoad |  | LN Reversed | CT L/N反接 | 32768
System fault word7 | Byte14 | bit0 | 暂无 |  | CT_LN_Reversed | CT LN Reversed | BMS COM Fault | BMS通信异常 | 1 | Y |  |  | System warning | Turn to Standby
|  | bit1 | 暂无 |  | PairingTimeOut | PairingTimeOut |  |  | 2 | Y
|  | bit2 | Error 312 | Warning 401 | MeterCommLoss | Warning 401 |  |  | 4
|  | bit3 |  |  | Meter2CommLoss |  | BAT NTC Open | 电池温度检测未接 | 8 | Y
|  | bit4 |  |  | SSTimeOut |  | SSTimeOut | 软起超时 | 16
|  | bit5 |  |  | \ |  |  |  | 32
|  | bit6 | Error 504 | Warning506 | BatTempOutRange | Warning506! | Warn 560 | 电池温度超范围 | 64
|  | bit7 | Error 507 | Warning508 | BatOutput_Overload | Over Load! | Over load | 输出过载 | 128 | Y | Y
| Byte15 | bit8 | 暂无 |  | BatteryFull |  | wBatteryFull | 电池充满 | 256 |  |  | Y | System warning | disharge only
|  | bit9 | 暂无 |  | BatteryNeedCharge |  |  |  | 512 |  |  | Y |  | force charge with 10%Pn
|  | bit10 | Error 500 | Warning 500 | BMSWarning | BMS Warning :XXX | BMS Warning :XXX | 电池管理系统信息异常 | 1024 |  |  | Y |  | BMSWarning
|  | bit11 | 暂无 |  | BatteryOnlyCharge |  |  |  | 2048 |  |  | Y |  | charge only
|  | bit12 | 暂无 |  | BatLowPower | BatLowPower |  |  | 4096 | Y |  |  |  | Need charge
|  | bit13 | Error 412 |  | NTCOpenWarning |  |  |  | 8192 | Y
|  | bit14 |  |  | \ |  |  |  | 16384
|  | bit15 |  |  | GridRelayOverCurrent |  |  |  | 32768

## MIX&SPA ErrorCode
Word definition |  | 逆变器故障码 | 逆变器告警码 | Total bit defined | Num | LCD_Display | Server Monitor | Monitor Chinese | Total bit defined | MIX defined | SPA defined | SPH defined | LED Display | Fault or warning bit | M3 | INV | SP | comment | Action
System fault word0 | Byte0 |  |  | Restart_Inv | 0. |  |  |  | Restart_Inv |  | BatVoltHigh_ISR |  |  | 1 |  |  |  | Internal fault | restart PWM
|  |  |  | Restart_SP | 1. |  |  |  | Restart_SP | Restart_SP | LLCOCP_FaultTZ |  |  | 2 |  |  | Y
|  | Error 508 |  | Bus2VoltHigh_ISR | 2. |  |  |  | Bus2VoltHigh_ISR | BusVoltHigh_TZ | Bus2VoltHigh_ISR | BusVoltHigh_TZ |  | 4 |  |  | Y
|  | Error 409 |  | BusVoltHigh_ISR | 3. |  | BusVoltHigh_ISR | BUS电压过大 | BusVoltHigh_ISR | BusVoltHigh__ISR | BusVoltHigh_Mask | BusVoltHigh__ISR |  | 8 |  | Y
|  | Error 416 |  | INVCurrOCP_Mask | 4. |  | INVCurrOCP_Mask | 逆变电流过大 | INVCurrOCP_Mask | INVCurrOCP_Mask | INVCurrOCP_Mask | INVCurrOCP_Mask |  | 16 |  | Y
|  | 未使用 |  | FreqUnstable_Mask | 5. |  |  |  | FreqUnstable_Mask | FreqUnstable_Mask | Reserved | FreqUnstable_Mask |  | 32 |  | Y
|  | Error 416 |  | BBOCP_FaultISR_SP | 6. |  | BBOCP_FaultISR_SP | buck_boost电流过大 | BBOCP_FaultISR_SP | BBOCP_FaultISR_SP | BBOCP_FaultISR_SP | BBOCP_FaultISR_SP |  | 64 |  |  | Y
|  | Error 416 |  | BBOCP_FaultTZ_SP | 7. |  | BBOCP_FaultTZ_SP | buck_boost电流过大 | BBOCP_FaultTZ_SP | BBOCP_FaultTZ_SP | BBOCP_FaultTZ_SP | BBOCP_FaultTZ_SP |  | 128 |  |  | Y
| Byte1 |  |  | GridZC_lossFault | 8. |  |  |  | GridZC_lossFault | GridZC_lossFault |  | GridZClossFault |  | 256 |  | Y |  | Grid side abnormal | Turn to Standby
|  |  |  | reserved | 9. |  |  |  | reserved |  |  |  |  | 512
|  |  |  | reserved | 10. |  |  |  | reserved |  |  |  |  | 1024
|  |  |  | reserved | 11. |  |  |  | reserved |  |  |  |  | 2048
|  | Error 300 |  | GridR_Vfault | 12. | AC V Outrange | AC V Outrange | 市电电压超范围 | GridR_Vfault | GridR_Vfault | GridR_VoltFault | GridR_Vfault |  | 4096 |  | Y
|  | Error 300 |  | GridS_VFault | 13. | AC V Outrange | AC V Outrange | 市电电压超范围 | GridS_VFault |  |  | GridS_VFault |  | 8192
|  | Error 300 |  | GridT_VFault | 14. | AC V Outrange | AC V Outrange | 市电电压超范围 | GridT_VFault |  |  | GridT_VFault |  | 16384
|  | Error 304 |  | GridFFault | 15. | AC F Outrange | AC F Outrange | 市电频率超范围 | GridFFault | GridFFault | GridFFault | GridFFault |  | 32768 |  | Y
System fault word1 | Byte2 |  |  | reserved | 0. |  |  |  | reserved |  |  |  |  | 1 |  |  |  | Grid side abnormal | Turn to Standby
|  | Error 201 |  | GFCIDamage | 1. |  |  |  | GFCIDamage |  |  | GFCIDamage |  | 2
|  | Error 300 |  | GridR_VLowFault | 2. | AC V Outrange | AC V Outrange | 市电电压超范围 | GridR_VLowFault |  |  | GridR_VLowFault |  | 4
|  | Error 300 |  | GridR_VHighFault | 3. | AC V Outrange | AC V Outrange | 市电电压超范围 | GridR_VHighFault |  |  | GridR_VHighFault |  | 8
|  | Error 300 |  | GridS_VLowFault | 4. | AC V Outrange | AC V Outrange | 市电电压超范围 | GridS_VLowFault |  |  | GridS_VLowFault |  | 16
|  | Error 300 |  | GridS_VHighFault | 5. | AC V Outrange | AC V Outrange | 市电电压超范围 | GridS_VHighFault |  |  | GridS_VHighFault |  | 32
|  | Error 300 |  | GridT_VLowFault | 6. | AC V Outrange | AC V Outrange | 市电电压超范围 | GridT_VLowFault |  |  | GridT_VLowFault |  | 64
|  | Error 300 |  | GridT_VHighFault | 7. | AC V Outrange | AC V Outrange | 市电电压超范围 | GridT_VHighFault |  |  | GridT_VHighFault |  | 128
| Byte3 | Error 416 |  | INVCurrOCP_ISR | 8. |  |  |  | INVCurrOCP_ISR |  |  | INVCurrOCP_ISR |  | 256 |  |  |  | Grid side abnormal | Turn to Standby
|  |  |  | INVCurrOCP_TZ | 9. |  |  |  | INVCurrOCP_TZ |  |  | INVCurrOCP_TZ |  | 512
|  |  |  | DCIHigh | 10. | Output High DCI | Output High DCI | 直流分量偏置异常 | DCIHigh | DCIHigh | DCIHigh | DCIHigh |  | 1024 |  | Y
|  |  |  | reserved | 11. |  |  |  | reserved |  |  |  |  | 2048
|  | Error 416 |  | INVR_CurrOCP_Rms | 12. |  |  |  | INVR_CurrOCP_Rms |  |  | INVR_CurrOCP_Rms |  | 4096
|  | Error 416 |  | INVS_CurrOCP_Rms | 13. |  |  |  | INVS_CurrOCP_Rms |  |  | INVS_CurrOCP_Rms |  | 8192
|  | Error 416 |  | INVT_CurrOCP_Rms | 14. |  |  |  | INVT_CurrOCP_Rms |  |  | INVT_CurrOCP_Rms |  | 16384
|  | Error 302 |  | NoUtility | 15. | No AC Connection | No AC Connection | 无市电连接 | NoUtility | NoUtility | NoUtility | NoUtility |  | 32768 |  | Y
System fault word2 | Byte4 | Error 304 |  | GridFLowFault | 0. | AC F Outrange | AC F Outrange | 市电频率超范围 | GridFLowFault |  |  | GridFLowFault |  | 1 |  |  |  | Grid side abnormal | Turn to Standby
|  | Error 304 |  | GridFHighFault | 1. | AC F Outrange | AC F Outrange | 市电频率超范围 | GridFHighFault |  |  | GridFHighFault |  | 2
|  | Error 313 |  | GridVolt_Unbalance_Fault | 2. |  |  |  | GridVolt_Unbalance_Fault |  |  | GridVolt_Unbalance_Fault |  | 4
|  | 暂无 |  | AC_PLL_Fault | 3. |  |  |  | AC_PLL_Fault |  |  | AC_PLL_Fault |  | 8
|  | 暂无 |  | OverLoadFault | 4. |  | OverLoadFault | 离网输出功率过大 | OverLoadFault |  |  | OverLoadFault |  | 16
|  | Error 311 |  | BackflowTimeOut | 5. | BackflowTimeOut |  |  | BackflowTimeOut |  |  |  |  | 32 |  | Y
|  |  |  | reserved | 6. |  |  |  | reserved |  |  |  |  | 64
|  |  |  | reserved | 7. |  |  |  | reserved |  |  |  |  | 128
| Byte5 | Error 604 |  | EPS_LineVoltR_Loss | 8. | EPS Volt Low ！ | EPS Volt Low | 离网输出电压过低 | EPS_LineVoltR_Loss | EPS_LineVoltR_Loss | EPS_LineVoltR_Loss | EPS_LineVoltR_Loss |  | 256 |  | Y |  | EPS side abnormal | Turn to Standby
|  | Error 604 |  | EPS_LineVoltS_Loss | 9. | EPS Volt Low ！ | EPS Volt Low | 离网输出电压过低 | EPS_LineVoltS_Loss |  |  | EPS_LineVoltS_Loss |  | 512
|  | Error 604 |  | EPS_LineVoltT_Loss | 10. | EPS Volt Low ！ | EPS Volt Low | 离网输出电压过低 | EPS_LineVoltT_Loss |  |  | EPS_LineVoltT_Loss |  | 1024
|  | Error 409 |  | EPS_BusVoltLow | 11. |  | EPS_BusVoltLow | 离网BUS电压过低 | EPS_BusVoltLow | EPS_BusVoltLow | EPS_BusVoltLow | EPS_BusVoltLow |  | 2048 |  | Y
|  | Error 607 |  | EPS_LoadAbnormal | 12. |  |  |  | EPS_LoadAbnormal | reserved | EPS_LoadAbnormal | EPS_LoadAbnormal |  | 4096 |  | Y
|  | Error 605 |  | EPS_LineVolt_High | 13. |  |  |  | EPS_LineVolt_High | EPS_LineVolt_High | EPS_LineVolt_High |  |  | 8192 |  | Y
|  | Error 606 |  | DCV_High | 14. |  |  |  | DCV_High | DCVHigh |  |  |  | 16384
|  | 暂无 |  | batteryOCP | 15. |  |  |  | batteryOCP | reserved |  | batteryOCP |  | 32768
System fault word3 | Byte6 | Error 505 |  | BatTerminalReversed | 0. | Battery reversed | Battery reversed | 电池反接 | BatTerminalReversed | BatTerminalReversed | BatTerminalReversed | BatTerminalReversed |  | 1 |  |  | Y | BAT Side abnormal | Turn to Standby
|  | Error 506 |  | Battery Open | 1. | Battery Open | Battery Open | 电池未接 | Battery Open | BMS Battery Open | Battery Open | Lithium_BatTerminalOpen |  | 2 |  |  | Y
|  | Error 502 |  | BatteryVoltageLow | 2. | Bat Voltage Low | Battery Voltage Low | 电池电压过低 | BatteryVoltageLow | BatteryVoltageLow | BatteryVoltageLow | BatteryVoltageLow |  | 4 |  |  | Y
|  |  |  | reserved | 3. |  | NV_OverTemp_Fault | 温度异常 | reserved | reserved | reserved | INV_OverTemp_Fault |  | 8 |  |  | Y
|  | Error 508 |  | reserved | 4. |  |  |  | reserved | reserved | reserved | BusVFault |  | 16
|  | Error 429 |  | SoftStartFail | 5. |  | NV_OverTemp_Fault | 软起失败 | SoftStartFail | SoftStartFail | SoftStartFail | SoftStartFail |  | 32 |  |  | Y
|  | Error 503 |  | BatteryVoltageHigh | 6. | Bat Voltage High | Bat Voltage High | 电池电压过高 | BatteryVoltageHigh | BatteryVoltageHigh | BatteryVoltageHigh | BatteryVoltageHigh |  | 64 |  |  | Y
|  |  |  | reserved | 7. |  |  |  | reserved | reserved |  |  |  | 128
| Byte7 | Error 501 |  | BMSError | 8. | BMS Error:XXX | BMS Battery Msg Failure | 电池管理系统信息异常 | BMSError | BMSError | BMSError | BMSError |  | 256 | Y |  |  | BAT Side abnormal | Turn to Standby
|  | Error 500 |  | BMS COM Fault | 9. | BMS COM Fault | BMS Error:XXX | 电池通讯故障 | BMS COM Fault | BMS COM Fault | BMS COM Fault | BMS COM Fault |  | 512 | Y
|  |  |  | \ | 10 |  | CT LN Reversed | 电流互感器反接 | \ | \ |  |  |  | 1024 | Y
|  |  |  | \ | 11 |  | PairingTimeOut | 无线CT配对超时 | \ | \ |  |  |  | 2048 | Y
|  |  |  | \ | 12 |  | Warn 401 | 通讯异常 | \ | \ |  |  |  | 4096 | Y
|  | 暂无 |  | BatterySleep | 13. |  | BatterySleep | 电池休眠 | BatterySleep | BatterySleep | BatterySleep | BatterySleep |  | 8192 | Y
|  | 暂无 |  | leadBAT NTC Open | 14. | BAT NTC Open ! | LeadacidBatNTCOpen | 铅酸电池NTC未接 | leadBAT NTC Open | LeadBAT NTC Open | LeadBAT NTC Open | LeadBAT NTC Open |  | 16384 | Y
|  |  |  | reserved | 15. |  |  |  | reserved |  |  |  |  | 32768
System fault word4 | Byte8 |  |  | reserved | 0. |  |  |  | reserved |  |  |  |  | 1 |  |  |  | PV Side Abnormal | Turn to Standby
|  |  |  | reserved | 1. |  |  |  | reserved |  |  |  |  | 2
|  |  |  | reserved | 2. |  |  |  | reserved |  |  |  |  | 4
|  |  |  | reserved | 3. |  |  |  | reserved |  |  |  |  | 8
|  |  |  | reserved | 4. |  |  |  | reserved |  |  |  |  | 16
|  | 暂无 |  | PV1_VoltLowWarn | 5. |  | PV1VoltLowWarn | PV1低压警告 | PV1_VoltLowWarn | PV1_VoltLowWarn |  | PV1_VoltLowWarn |  | 32 |  | Y
|  | 暂无 |  | PV2-VoltLowWarn | 6. |  | PV2VoltLowWarn | PV2低压警告 | PV2-VoltLowWarn | PV2-VoltLowWarn |  | PV2-VoltLowWarn |  | 64 |  | Y
|  |  |  | reserved | 7. |  |  |  | reserved |  |  |  |  | 128
| Byte9 |  |  | reserved | 8. |  |  |  | reserved |  |  |  |  | 256 |  |  |  | PV Side Abnormal | Turn to Standby
|  |  |  | reserved | 9. |  |  |  | reserved |  |  |  |  | 512
|  |  |  | reserved | 10. |  |  |  | reserved |  |  |  |  | 1024
|  |  |  | reserved | 11. |  |  |  | reserved |  |  |  |  | 2048
|  |  |  | reserved | 12. |  |  |  | reserved |  |  |  |  | 4096
|  |  |  | reserved | 13. |  |  |  | reserved |  |  |  |  | 8192
|  |  |  | reserved | 14. |  |  |  | reserved |  |  |  |  | 16384
|  |  |  | reserved | 15. |  |  |  | reserved |  |  |  |  | 32768
System fault word5 | Byte10 | Error 402 |  | NE DetectFault | 0. | Error 303 | Error 303 | 零地侦测异常 | NE DetectFault | NE DetectFault | NE DetectFault | NE DetectFault |  | 1 |  |  | Y | Sytem fault | Turn to Standby
|  | Error 203 |  | PVISOFault | 1. | PV Isolation Low | PV Isolation Low | 面板绝缘阻抗低 | PVISOFault | PVISOFault |  | PVISOFault |  | 2 |  | Y
|  | Error 412 |  | RelayFault | 2. | Error 405 | Error 405 | 继电器异常 | RelayFault | RelayFault | RelayFault | RelayFault |  | 4 |  | Y
|  | Error 409 |  | BusVoltHighFault_ISR | 3. | Error：103！ | Error 417 | DSP和M3对电网电压采样不一致 | BusVoltHighFault_ISR |  |  | BusVoltHighFault_ISR |  | 8
|  | Error 202 |  | BusSampleFault | 4. | Error：105！ | Error 419 | BUS电压采样不一致 | BusSampleFault |  |  | BusSampleFault |  | 16
|  | Error 408 |  | DSP_M3FWUnmatch | 5. | Error 418 | Error 418 | 控制板与通讯板固件版本不匹配 | DSP_M3FWUnmatch | DSP_M3FWUnmatch | DSP_M3FWUnmatch | DSP_M3FWUnmatch |  | 32 | Y
|  | Error 408 |  | AComFault | 6. | Error 411 | Error 411 | 内部通讯异常 | AComFault | AComFault | AComFault | AComFault |  | 64 | Y
|  | Error 408 |  | BComFault | 7. | Error 411 | Error 411 | 内部通讯异常 | BComFault | BComFault | BComFault | BComFault |  | 128 | Y
| Byte11 | Error 600 |  | EPS_OPShortFault | 8. | OP Short Fault ! | EPS OP Short Fault | 离网短路 | EPS_OPShortFault | EPS_OPShortFault | EPS_OPShortFault | EPS_OPShortFault |  | 256 |  | Y |  | Sytem fault | Turn to Standby
|  | Error 407 |  | AuotTestFault | 9. | Error 407 | Error 407 | 自动检测失败 | AuotTestFault | AuotTestFault | AuotTestFault | AuotTestFault |  | 512 |  | Y
|  | Error 406 |  | ModelFault | 10. | Error 406 | Init model fault | 初始化模式异常 | ModelFault | ModelFault | ModelFault | ModelFault |  | 1024 |  | Y | Y
|  | Error 405 |  | NTCOpenFault | 11. | NTC Open | NTC Open | 温度异常 | NTCOpenFault | NTCOpenFault | NTCOpenFault | NTCOpenFault |  | 2048 |  | Y | Y
|  | Error 428 |  | BusUnbalance_Fault | 12. | BusUnbalance |  |  | BusUnbalance_Fault | reserved | reserved | BusUnbalance_Fault |  | 4096 |  |  | Y
|  | Error 418 |  | BBHeatsink_TempOver | 13. | Error:408! |  |  | BBHeatsink_TempOver | BBHeatsink_TempOver | LLC Heatsink_TempOver | BBHeatsink_TempOver |  | 8192 |  |  | Y
|  |  | Warning 203 | Grid voltage sampling | 14. |  |  |  | Grid voltage sampling | reserved |  |  |  | 16384
|  |  | Warning 203 | reserved | 15. |  |  |  | reserved | reserved |  |  |  | 32768
System fault word6 | Byte12 | Error 303 |  | PV1_VoltHighFault | 0. | PV Voltage High! | PVVoltHigh_Fault | PV1电压过高 | PV1_VoltHighFault | PV1_VoltHighFault |  | PV1_VoltHighFault |  | 1 |  | Y |  | Sytem fault | Turn to Standby
|  |  |  | PV2_VoltHighFault | 1. | PV Voltage High! | PV2_VoltHighFault | PV2电压过高 | PV2_VoltHighFault | PV2_VoltHighFault |  | PV2_VoltHighFault |  | 2
|  | Error 411 |  | BTHeatsink_Overtemp | 2. | Error:408! | Over Temperature | 温度异常 | BTHeatsink_Overtemp | BTHeatsink_Overtemp |  | BTHeatsink_Overtemp |  | 4 |  | Y
|  | Error 411 |  | INVHeatsink_Overtemp | 3. | Error:408! | Over Temperature | 温度异常 | INVHeatsink_Overtemp | INVHeatsink_Overtemp | INVHeatsink_Overtemp | INVHeatsink_Overtemp |  | 8 |  | Y
|  | 暂无 |  | MasterForceINVFault | 4. |  | MasterForceINVFault | INV发生故障 | MasterForceINVFault | MasterForceINVFault | MasterForceINVFault | MasterForceINVFault |  | 16 |  | Y
|  | 暂无 |  | MasterForceSPFault | 5. |  | MasterForceSPFault | SP发生故障 | MasterForceSPFault | MasterForceSPFault | MasterForceSPFault | MasterForceSPFault |  | 32 |  |  | Y
|  | Error 201 |  | GFCIHigh | 6. | Residual I High | Leakage current too high | 漏电流过高 | GFCIHigh | GFCIHigh | GFCIHigh | GFCIHigh |  | 64 |  | Y
|  | 暂无 |  | reserved | 7. |  |  |  | reserved |  |  |  |  | 128
| Byte13 |  | Warning 205 | BoostDriver1Warn | 8. | 不显示 |  |  | BoostDriver1Warn |  |  | BoostDriver1Warn |  | 256 |  |  |  | System warning | Turn to Standby
|  |  | Warning 205 | BoostDriver2Warn | 9. | 不显示 |  |  | BoostDriver2Warn |  |  | BoostDriver2Warn |  | 512
|  |  |  | reserved | 10. | Warn: 104! |  |  | reserved |  |  |  |  | 1024
|  |  |  | PV1_ShortFault | 11. | Warning 203 | Warning 203 | PV端短路告警 | PV1_ShortFault | PV1_ShortFault |  | PV1_ShortFault |  | 2048 |  | Y
|  |  |  | PV2_ShortFault | 12. | Warning 203 | Warning 203 | PV端短路告警 | PV2_ShortFault | PV2_ShortFault |  | PV2_ShortFault |  | 4096 |  | Y
|  |  |  | reserved | 13. |  | Warn 101 | 无线CT/电表通信异常 | reserved |  |  |  |  | 8192
|  |  |  | reserved | 14. |  |  |  | reserved |  |  |  |  | 16384
|  |  |  | reserved | 15. |  | LN Reversed | CT L/N反接 | reserved |  |  | CT_LN_Reversed |  | 32768
System fault word7 | Byte14 | 暂无 |  | CT_LN_Reversed | 0 | CT LN Reversed | BMS COM Fault | BMS通信异常 | CT_LN_Reversed | CT_LN_Reversed | CT_LN_Reversed |  | CT反接 | 1 |  |  |  | System warning | Turn to Standby
|  | 暂无 |  | PairingTimeOut | 1 | PairingTimeOut |  |  | PairingTimeOut | PairingTimeOut | PairingTimeOut | PairingTimeOut |  | 2
|  | Error 312 | Warning 401 | MeterCommLoss | 2 | Warning 401 |  |  | MeterCommLoss | MeterCommLoss | MeterCommLoss | MeterCommLoss |  | 4
|  |  |  | BAT NTC Open | 3. | BAT NTC Open | BAT NTC Open | 电池温度检测未接 | BAT NTC Open | BAT NTC Open |  | BAT NTC Open |  | 8 | Y
|  |  |  | SS Timeout | 4. | 不显示，重启 | SSTimeOut | 软起超时 | SS Timeout | reserved |  | SS Timeout |  | 16
|  |  |  | reserved | 5. |  |  |  | reserved | reserved |  |  |  | 32
|  | Error 504 | Warning506 | BatTempOutRange | 6. | warning506! | Warn 560 | 电池温度超范围 | BatTempOutRange | BatTempOutRange | BatTempOutRange | BatTOutRange |  | 64
|  | Error 507 | Warning508 | BATOutput_Overload | 7. | Over Load! | Over load | 输出过载 | BATOutput_Overload | BATOutput_Overload | BATOutput_Overload | BATOutput_Overload |  | 128 | Y | Y
| Byte15 | 暂无 |  | wBatteryFull | 8. |  | wBatteryFull | 电池充满 | wBatteryFull | wBatteryFull | wBatteryFull | wBatteryFull |  | 256 |  |  | Y | System warning | disharge only
|  | 暂无 |  | wBatteryNeedCharge | 9. |  |  |  | wBatteryNeedCharge | wBatteryNeedCharge | wBatteryNeedCharge | wBatteryNeedCharge |  | 512 |  |  | Y |  | force charge with 10%Pn
|  | Error 500 | Warning 500 | BMSWarning | 10. | BMS Warning :XXX | BMS Warning :XXX | 电池管理系统信息异常 | BMSWarning | BMSWarning | BMSWarning | BMSWarning |  | 1024 |  |  | Y |  | unused
|  | 暂无 |  | wBatteryOnlyCharge | 11. |  |  |  | wBatteryOnlyCharge | BatteryOnlyCharge | wBatteryOnlyCharge |  |  | 2048 |  |  | Y |  | charge only
|  | 暂无 |  | BatLowPower | 12. | BatLowPower |  |  | BatLowPower | reserved | BatLowPower |  |  | 4096 | Y |  |  |  | Need charge
|  | Error 412 |  | InterNTCOpenWarning | 13. |  |  |  | InterNTCOpenWarning |  | InterNTCOpenWarning |  |  | 8192 | Y
|  |  |  | reserved | 14. |  |  |  | reserved |  |  |  |  | 16384
|  |  |  | reserved | 15. |  |  |  | reserved |  |  |  |  | 32768
差异化项目
Note on M94: 古瑞瓦特新能源股份有限公司: SPH4-11K bus不平衡故障

## SPH3~6k BL UP&US
Word definition |  |  | 逆变器故障码 | 逆变器告警码 | Total bit defined | LCD_Display （old） | Server Monitor（old） | Monitor Chinese（old） | Server Monitor（new） | Monitor Chinese（new） | Fault or warning Data | M3 | INV | SP | SPH3~6k BL UP | comment | Action
System fault word0 | Byte0 | bit0 | Error 503 |  | BatVoltHigh_ISR |  |  |  | Error 503 | Error 503 | 1 |  |  | Y |  | Internal fault | restart PWM
|  | bit1 |  |  | \ |  |  |  | \ | \ | 2 |  |  |  | 未启用
|  | bit2 | Error 508 |  | Bus2VoltHigh_ISR |  |  |  | Error 508 | Error 508 | 4 |  |  | Y
|  | bit3 | Error 409 |  | BusVoltHigh_ISR |  | BusVoltHigh_ISR | BUS电压过大 | Error 409 | Error 409 | 8 |  | Y
|  | bit4 | Error 416 |  | INVCurrOCP_TZ |  | INVCurrOCP_Mask | 逆变电流过大 | Error 416 | Error 416 | 16 |  | Y
|  | bit5 | 未使用 |  | FreqUnstable_Mask |  |  |  | \ | \ | 32 |  |  |  | 未启用
|  | bit6 | Error 416 |  | BBOCP_FaultISR |  | BBOCP_FaultISR_SP | buck_boost电流过大 | Error 416 | Error 416 | 64 |  |  | Y
|  | bit7 | Error 416 |  | BDCOCP_FaultTZ |  | BBOCP_FaultTZ_SP | buck_boost电流过大 | Error 416 | Error 416 | 128 |  |  |  | 未启用
| Byte1 | bit8 |  |  | GridZC_lossFault | [5 empty] | 256 |  |  |  | 未启用 | Grid side abnormal | Turn to Standby
|  | bit9 |  |  | \ |  |  |  | \ | \ | 512 |  |  |  | 未启用
|  | bit10 |  |  | \ |  |  |  | \ | \ | 1024 |  |  |  | 未启用
|  | bit11 |  |  | \ |  |  |  | \ | \ | 2048 |  |  |  | 未启用
|  | bit12 | Error 300 |  | GridR_VFault(Singlephase) | AC V Outrange | AC V Outrange | 市电电压超范围 | Error 300 | Error 300 | 4096 |  | Y
|  | bit13 | Error 300 |  | GridS_VFault | AC V Outrange | AC V Outrange | 市电电压超范围 | Error 300 | Error 300 | 8192 |  |  |  | 未启用
|  | bit14 | Error 300 |  | GridT_VFault | AC V Outrange | AC V Outrange | 市电电压超范围 | Error 300 | Error 300 | 16384 |  |  |  | 未启用
|  | bit15 | Error 304 |  | GridFFault | AC F Outrange | AC F Outrange | 市电频率超范围 | Error 304 | Error 304 | 32768 |  | Y
System fault word1 | Byte2 | bit0 |  |  | reserved |  |  |  | \ | \ | 1 |  |  |  | 未启用 | Grid side abnormal | Turn to Standby
|  | bit1 | Error 201 |  | GFCIDamage |  |  |  | Error 201 | Error 201 | 2 |  |  |  | 未启用
|  | bit2 | Error 300 |  | GridR_VLowFault | AC V Outrange | AC V Outrange | 市电电压超范围 | Error 300 | Error 300 | 4 |  |  |  | 未启用
|  | bit3 | Error 300 |  | GridR_VHighFault | AC V Outrange | AC V Outrange | 市电电压超范围 | Error 300 | Error 300 | 8 |  |  |  | 未启用
|  | bit4 | Error 300 |  | GridS_VLowFault | AC V Outrange | AC V Outrange | 市电电压超范围 | Error 300 | Error 300 | 16 |  |  |  | 未启用
|  | bit5 | Error 300 |  | GridS_VHighFault | AC V Outrange | AC V Outrange | 市电电压超范围 | Error 300 | Error 300 | 32 |  |  |  | 未启用
|  | bit6 | Error 300 |  | GridT_VLowFault | AC V Outrange | AC V Outrange | 市电电压超范围 | Error 300 | Error 300 | 64 |  |  |  | 未启用
|  | bit7 | Error 300 |  | GridT_VHighFault | AC V Outrange | AC V Outrange | 市电电压超范围 | Error 300 | Error 300 | 128 |  |  |  | 未启用
| Byte3 | bit8 | Error 416 |  | INVCurrOCP_ISR |  |  |  | Error 416 | Error 416 | 256 |  |  |  | 未启用 | Grid side abnormal | Turn to Standby
|  | bit9 |  |  | \ |  |  |  | \ | \ | 512 |  |  |  | 未启用
|  | bit10 |  |  | \ |  | Output High DCI | 直流分量偏置异常 | \ | \ | 1024 |  |  |  | 未启用
|  | bit11 |  |  | \ |  |  |  | \ | \ | 2048 |  |  |  | 未启用
|  | bit12 | Error 416 |  | INVR_CurrOCP_Rms |  |  |  | Error 416 | Error 416 | 4096 |  |  |  | 未启用
|  | bit13 | Error 416 |  | INVS_CurrOCP_Rms |  |  |  | Error 416 | Error 416 | 8192 |  |  |  | 未启用
|  | bit14 | Error 416 |  | INVT_CurrOCP_Rms |  |  |  | Error 416 | Error 416 | 16384 |  |  |  | 未启用
|  | bit15 | Error 302 |  | NoUtility | No AC Connection | No AC Connection | 无市电连接 | Error 302 | Error 302 | 32768 |  | Y
System fault word2 | Byte4 | bit0 | Error 304 |  | GridFLowFault | AC F Outrange | AC F Outrange | 市电频率超范围 | Error 304 | Error 304 | 1 |  |  |  | 未启用 | Grid side abnormal | Turn to Standby
|  | bit1 | Error 304 |  | GridFHighFault | AC F Outrange | AC F Outrange | 市电频率超范围 | Error 304 | Error 304 | 2 |  |  |  | 未启用
|  | bit2 | Error 313 |  | GridVolt_Unbalance_Fault |  |  |  | Error 313 | Error 313 | 4 |  |  |  | 未启用
|  | bit3 | 暂无 |  | AC_PLL_Fault |  |  |  | \ | \ | 8 |  |  |  | 未启用
|  | bit4 | 暂无 |  | OverLoadFault |  | OverLoadFault | 离网输出功率过大 |  |  | 16 |  |  |  | 未启用
|  | bit5 | Error 311 |  | BackflowTimeOut | BackflowTimeOut |  |  | Error 311 | Error 311 | 32 |  | Y
|  | bit6 |  |  | \ |  |  |  | \ | \ | 64 |  |  |  | 未启用
|  | bit7 |  |  | \ |  |  |  | \ | \ | 128 |  |  |  | 未启用
| Byte5 | bit8 | Error 604 |  | EPS_LineVoltR_Loss | U(E)PS Volt Low ！ | EPS Volt Low | 离网输出电压过低 | Error 604 | Error 604 | 256 |  | Y |  |  | EPS side abnormal | Turn to Standby
|  | bit9 | Error 604 |  | EPS_LineVoltS_Loss EPSOverWatt(单相机) | U(E)PS Volt Low ！ | EPS Volt Low | 离网输出电压过低 | Error 604 | Error 604 | 512 |  | Y
|  | bit10 | Error 604 |  | EPS_LineVoltT_Loss | U(E)PS Volt Low ！ | EPS Volt Low | 离网输出电压过低 | Error 604 | Error 604 | 1024 |  |  |  | 未启用
|  | bit11 | Error 409 |  | EPS_BusVoltLow |  | EPS_BusVoltLow | 离网BUS电压过低 | Error 409 | Error 409 | 2048 |  | Y
|  | bit12 | Error 607 |  | EPS_LoadAbnormal |  |  |  | Error 607 | Error 607 | 4096 |  |  |  | 未启用
|  | bit13 | Error 605 |  | EPS_LineVolt_High |  |  |  | Error 605 | Error 605 | 8192 |  | Y
|  | bit14 | Error 606 |  | DCV_High |  |  |  | Error 606 | Error 606 | 16384 |  |  |  | 未启用
|  | bit15 | 暂无 |  | Bat_OCP |  |  |  | \ | \ | 32768 |  |  |  | 未启用
System fault word3 | Byte6 | bit0 | Error 505 |  | BatTerminalReverse | Battery reversed | Battery reversed | 电池反接 | Error 505 | Error 505 | 1 |  |  | Y |  | BAT Side abnormal | Turn to Standby
|  | bit1 | Error 506 |  | BatTerminalOpen | Battery Open | Battery Open | 电池未接 | Error 506 | Error 506 | 2 |  |  | Y
|  | bit2 | Error 502 |  | BatVoltLow | Bat Voltage Low | Battery Voltage Low | 电池电压过低 | Error 502 | Error 502 | 4 |  |  | Y
|  | bit3 |  |  | \ |  | NV_OverTemp_Fault | 温度异常 | \ | \ | 8 |  |  |  | 未启用
|  | bit4 | Error 508 |  | BUS2Abnomal |  |  |  | Error 508 | Error 508 | 16 |  |  | Y
|  | bit5 | Error 429 |  | SoftStartFail |  | NV_OverTemp_Fault | 软起失败 | Error 429 | Error 429 | 32 |  |  | Y
|  | bit6 | Error 503 |  | BatVoltHigh | Bat Voltage High | Bat Voltage High | 电池电压过高 | Error 503 | Error 503 | 64 |  |  | Y
|  | bit7 | 暂无 |  | BatOverLoadFault | Bat overLoad |  |  | Battery Over Load | 电池过载 | 128 |  |  | Y
| Byte7 | bit8 | Error 501 |  | BMSError | BMS Error:XXX | BMS Battery Msg Failure | 电池管理系统信息异常 | Error 501 | Error 501 | 256 | Y |  |  |  | BAT Side abnormal | Turn to Standby
|  | bit9 | Error 500 |  | BMS CommFault | BMS COM Fault | BMS Error:XXX | 电池通讯故障 | Error 500 | Error 500 | 512 | Y
|  | bit10 |  |  | \ |  | CT LN Reversed | 电流互感器反接 | \ | \ | 1024 |  |  |  | 未启用
|  | bit11 |  |  | \ |  | PairingTimeOut | 无线CT配对超时 | \ | \ | 2048 |  |  |  | 未启用
|  | bit12 |  |  | \ |  | Warn 401 | 通讯异常 | \ | \ | 4096 |  |  |  | 未启用
|  | bit13 | 暂无 |  | BatSleep |  | BatterySleep | 电池休眠 | BatterySleep | 电池休眠 | 8192 | Y
|  | bit14 | 暂无 |  | BatNTCOpen | BAT NTC Open ! | LeadacidBatNTCOpen | 铅酸电池NTC未接 | LeadacidBatNTCOpen | 铅酸电池NTC未接 | 16384 | Y
|  | bit15 |  |  | BMSStateAbnormal | [5 empty] | 32768 |  |  | Y
System fault word4 | Byte8 | bit0 |  |  | \ | [5 empty] | 1 |  |  |  |  | PV Side Abnormal | Turn to Standby
|  | bit1 |  |  | \ | [5 empty] | 2
|  | bit2 |  |  | \ | [5 empty] | 4
|  | bit3 |  |  | \ | [5 empty] | 8
|  | bit4 |  |  | \ | [5 empty] | 16
|  | bit5 | 暂无 |  | PV1_VoltLowWarn |  | PV1VoltLowWarn | PV1低压警告 | PV1VoltLowWarn | PV1低压警告 | 32 |  | Y
|  | bit6 | 暂无 |  | PV2-VoltLowWarn |  | PV2VoltLowWarn | PV2低压警告 | PV2VoltLowWarn | PV2低压警告 | 64 |  |  |  | 未启用
|  | bit7 |  |  | \ | [5 empty] | 128 |  |  |  | 未启用
| Byte9 | bit8 |  |  | \ | [5 empty] | 256 |  |  |  | 未启用 | PV Side Abnormal | Turn to Standby
|  | bit9 |  |  | \ | [5 empty] | 512 |  |  |  | 未启用
|  | bit10 |  |  | \ | [5 empty] | 1024 |  |  |  | 未启用
|  | bit11 |  |  | \ | [5 empty] | 2048 |  |  |  | 未启用
|  | bit12 |  |  | \ | [5 empty] | 4096 |  |  |  | 未启用
|  | bit13 |  |  | \ | [5 empty] | 8192 |  |  |  | 未启用
|  | bit14 |  |  | \ | [5 empty] | 16384 |  |  |  | 未启用
|  | bit15 |  |  | \ | [5 empty] | 32768 |  |  |  | 未启用
System fault word5 | Byte10 | bit0 | Error 402 |  | DCIHigh | Output High DCI | Error 303 | 零地侦测异常 | Error 402 | Error 402 | 1 |  |  | Y |  | Sytem fault | Turn to Standby
|  | bit1 | Error 203 |  | PVISOFault | PV Isolation Low | PV Isolation Low | 面板绝缘阻抗低 | Error 203 | Error 203 | 2 |  | Y
|  | bit2 | Error 412 |  | NTCOpenFault | NTC Open | Error 405 | 继电器异常 | Error 412 | Error 412 | 4 |  | Y | Y
|  | bit3 | Error 409 |  | BusVoltHigh_Fault | Error：103！ | Error 417 | DSP和M3对电网电压采样不一致 | Error 409 | Error 409 | 8 |  | Y
|  | bit4 | Error 202 |  | PVVoltHigh_Fault | PV Voltage High! | Error 419 | BUS电压采样不一致 | Error 202 | Error 202 | 16 |  | Y
|  | bit5 | Error 408 |  | BTHeatsink_Overtemp | Error:408! | Error 418 | 控制板与通讯板固件版本不匹配 | Error 408 | Error 408 | 32 |  | Y
|  | bit6 | Error 408 |  | BBHeatsink_TempOver | Error:408! | Error 411 | 内部通讯异常 | Error 408 | Error 408 | 64 |  |  | Y
|  | bit7 | Error 408 |  | INVHeatsink_Overtemp | Error:408! | Error 411 | 内部通讯异常 | Error 408 | Error 408 | 128 |  | Y
| Byte11 | bit8 | Error 600 |  | EPS_OPShortFault | OP Short Fault ! | EPS OP Short Fault | 离网短路 | Error 600 | Error 600 | 256 |  | Y |  |  | Sytem fault | Turn to Standby
|  | bit9 | Error 407 |  | AuotTestFault | Error 407 | Error 407 | 自动检测失败 | Error 407 | Error 407 | 512 |  | Y
|  | bit10 | Error 406 |  | ModelFault | Error 406 | Init model fault | 初始化模式异常 | Error 406 | Error 406 | 1024 |  | Y
|  | bit11 | Error 405 |  | RelayFault | Error 405 | NTC Open | 温度异常 | Error 405 | Error 405 | 2048 |  | Y
|  | bit12 | Error 428 |  | BusUnbalance_Fault | BusUnbalance |  |  | Error 428 | Error 428 | 4096
|  | bit13 | Error 418 |  | DSP_M3FWUnmatch | Error 418 |  |  | Error 418 | Error 418 | 8192 | Y
|  | bit14 |  | Warning 203 | PV1Short_Fault | Warning 203 |  |  | Warning 203 | Warning 203 | 16384 |  | Y
|  | bit15 |  | Warning 203 | PV2Short_Fault | Warning 203 |  |  | Warning 203 | Warning 203 | 32768 |  | Y
System fault word6 | Byte12 | bit0 | Error 303 |  | NEDetectFault | Error 303 | PVVoltHigh_Fault | PV1电压过高 | Error 303 | Error 303 | 1 |  |  | Y |  | Sytem fault | Turn to Standby
|  | bit1 |  |  | AFCICheckFault（US） |  | PV2_VoltHighFault | PV2电压过高 |  |  | 2
|  | bit2 | Error 411 |  | AComFault | Error 411 | Over Temperature | 温度异常 | Error 411 | Error 411 | 4 | Y
|  | bit3 | Error 411 |  | BComFault AFCIFault（US） | Error 411 | Over Temperature | 温度异常 | Error 411 | Error 411 | 8
|  | bit4 | 暂无 |  | MasterForceINVFault |  | MasterForceINVFault | INV发生故障 | MasterForceINVFault | 远程关机 | 16 | Y
|  | bit5 | 暂无 |  | MasterForceSPFault |  | MasterForceSPFault | SP发生故障 | MasterForceSPFault | 远程关机 | 32 | Y
|  | bit6 | Error 201 |  | GFCIHigh | Residual I High | Leakage current too high | 漏电流过高 | Error 201 | Error 201 | 64 |  | Y
|  | bit7 | 暂无 |  | VirLoad_Overtemp | VirLoad TempOver |  |  |  |  | 128
| Byte13 | bit8 |  | Warning 205 | BoostDriver1Warn | 不显示 |  |  | Warning 205 | Warning 205 | 256 |  |  |  |  | System warning | Turn to Standby
|  | bit9 |  | Warning 205 | BoostDriver2Warn | 不显示 |  |  | Warning 205 | Warning 205 | 512
|  | bit10 |  |  | \ | [5 empty] | 1024
|  | bit11 |  |  | SPDFault | SPD Fault | Warning 203 | PV端短路告警 |  |  | 2048 |  | Y
|  | bit12 |  |  | \ |  | Warning 203 | PV端短路告警 |  |  | 4096
|  | bit13 |  |  | \ |  | Warn 101 | 无线CT/电表通信异常 |  |  | 8192
|  | bit14 |  |  | \ | [5 empty] | 16384
|  | bit15 |  |  | EPSoverLoad |  | LN Reversed | CT L/N反接 |  |  | 32768
System fault word7 | Byte14 | bit0 | 暂无 |  | CT_LN_Reversed | CT LN Reversed | BMS COM Fault | BMS通信异常 |  |  | 1 | Y |  |  |  | System warning | Turn to Standby
|  | bit1 | 暂无 |  | PairingTimeOut | PairingTimeOut |  |  |  |  | 2 | Y
|  | bit2 | Error 312 | Warning 401 | MeterCommLoss | Warning 401 |  |  | Warning 401 | Warning 401 | 4 | Y
|  | bit3 |  | Warning 401 | Meter2CommLoss | Warning 401 | BAT NTC Open | 电池温度检测未接 | Warning 401 | Warning 401 | 8 | Y
|  | bit4 |  |  | SSTimeOut |  | SSTimeOut | 软起超时 |  |  | 16
|  | bit5 |  |  | \ | [5 empty] | 32
|  | bit6 | Error 504 | Warning506 | BatTempOutRange | Warning506! | Warn 560 | 电池温度超范围 |  |  | 64
|  | bit7 | Error 507 | Warning508 | BatOutput_Overload | Over Load! | Over load | 输出过载 |  |  | 128 |  | Y
| Byte15 | bit8 | 暂无 |  | BatteryFull |  | wBatteryFull | 电池充满 |  |  | 256 |  |  | Y |  | System warning | disharge only
|  | bit9 | 暂无 |  | BatteryNeedCharge | [5 empty] | 512 |  |  | Y |  |  | force charge with 10%Pn
|  | bit10 | Error 500 | Warning 500 | BMSWarning | BMS Warning :XXX | BMS Warning :XXX | 电池管理系统信息异常 |  |  | 1024 | Y |  |  |  |  | BMSWarning
|  | bit11 | 暂无 |  | BatteryOnlyCharge | [5 empty] | 2048 |  |  | Y |  |  | charge only
|  | bit12 | 暂无 |  | BatLowPower | BatLowPower |  |  |  |  | 4096 | [5 empty] | Need charge
|  | bit13 | Error 412 |  | NTCOpenWarning |  |  |  | Error 412 | Error 412 | 8192 | Y
|  | bit14 |  |  | EPSOverCurrentWarn |  |  |  | EPS Over Current Warn | 离网过流告警 | 16384 |  |  | Y
|  | bit15 |  |  | GridRelayOverCurrent |  |  |  | Grid Relay Over Current | 网测继电器过流 | 32768 |  | Y